HEALTH, SAFETY & ENVIRONMENT MANAGEMENT SYSTEM

DAN HSE Minimum Requirements

Compressed Gas Cylinders

Document Control

| Document No. | 01-000001-000000-DAN-HSE-MNR-000006 | Revision | R01 |
| --- | --- | --- | --- |
| Issue Date | June 2026 | Classification | Controlled — Internal |
| Document Owner | HSSE Department | Page Format | US Letter |

Table of Contents

Purpose

Scope

Definitions

Standards

Tools and References

1.0 General Requirements

2.0 Storage

3.0 Handling of Cylinders

4.0 Transportation

Revision History

# Purpose

The purpose of this HSE minimum requirement is to define the requirements for the safe use and operations of Compressed Gas Cylinders required on DAN projects.

# Scope

This HSE Minimum Requirement is applicable to all parties’ personnel who are working within DAN Company Projects.

# Definitions

| Term | Definition |
| --- | --- |
| Compressed Gas Cylinders | Compressed gasses are gasses that are stored under pressure in cylinders. The three major types of compressed gasses are liquefied gasses, non-liquefied gasses, and dissolved gasses |

# Standards

- DAN Construction HSE Management System Manual (01-000001-000000-DAN-HSE-MAN-000001) and management procedures.

- Saudi Labour Law – Royal Decree No. M/51, 23 Sha’ban 1426 / 27 September 2005

# Tools and References

- Compressed Gas Cylinder Inspection Records

- OSHA standard 1910.101 Compressed gases (general requirements).

# 1.0 General Requirements

- Specific competency-based training will be provided to all persons involved in handling, transporting, and using compressed gas cylinders, these include Managers, Supervisors, Logistics, Storekeepers, and Workers.

- Compressed gas cylinders shall be properly marked or labeled, including their contents, with lettering in Arabic and English.

- Cylinders shall not be placed in confined spaces or adjacent to excavations.

- Cylinders shall be inspected for damage, severe corrosion, valve leakage, and current hydro-test date before each use.

- A leaking cylinder shall be immediately removed to an open space, clear of all buildings, people, and any potential source of ignition.

- All cylinders shall have an approved pressure-reducing regulator with a check valve connected to the cylinder valve.

- Oil, grease, or other hydrocarbons shall not be used as a lubricant on valves, fittings, or threaded attachments.

- Regulators, gauges, safety valves, hoses, and connections must be clearly marked with the manufacturers’ rating / international standard, uniquely tagged, coded to demonstrate the period of the last inspection, protect from environmental hazards, and be free from damage.

- LPG must not be used on-site without Civil Defence Approvals

- Compressed gas cylinders must be:

- Considered full and the valves protected

- Moved using specific racks/equipment to protect the valve connection

- Kept in storage areas that clearly identify the type of gas being stored

- Stored vertically in open and secure compound/cradles in a manner that prevents them from falling over

- Operated using approved keys or handles, they must remain with the compressed cylinder while in use

- Disposed of using approved supplier/vendor

# 2.0 Storage

- Cylinders shall be stored in a safe and accessible location. Cylinder storage locations shall be a dry, well-ventilated area prepared and reserved for that purpose.

- Flammable/combustible substances (e.g., oil, grease, volatile liquids) and corrosive substances shall not be stored in the same area as gas cylinders.

- Oxygen cylinders and cylinders containing other oxidizers (e.g., chlorine, nitrous oxide) shall be stored at least 6.1 m (20 ft) from flammable gas cylinders or they shall be separated by a ½-hour fire-rated barrier at least 1.5 m (5 ft) high.

- Smoking and other sources of ignition are prohibited near storage areas.

- Storage areas shall have Arabic, English, and the languages of all workers’ “No Smoking” and “Gas Cylinder Storage Area” signs prominently displayed.

- Cylinders shall be chained or otherwise secured in an upright position; use bottle/cylinder racks wherever possible.

- Cylinders stored in the open shall not have direct contact with the ground, exposure to extreme weather, or contact with water.

- The number of cylinders shall be kept to a minimum at job site locations. Bulk storage (e.g., large inventories) shall be located off-site.

- When regulators are removed from the cylinders, they shall be considered “not in use” or “stored” and cylinder valve caps shall be put back in place.

- Water and dry chemical fire extinguishers shall be immediately available within 15m(50ft) of the storage area.

- Cylinders shall not be stored at temperatures or locations that could result in the temperature of the cylinder exceeding 54 °C (130 °F). Outside cylinder storage areas shall have protective enclosures or sun shelters installed as needed to prevent cylinders from reaching 54 °C (130 °F).

- Cylinders shall not be stored in a location where they would be subject to direct flames or other heat sources, such as furnaces.

- Empty and full cylinders shall be stored separately with empty cylinders plainly marked to avoid confusion.

- Cylinders (empty and full) shall be segregated according to the type of gas they contain.

- Storage Room

- Cylinder storage rooms shall be sufficiently ventilated so that explosive concentrations of the gas cannot accumulate.

- Electrical systems (wiring, connections, conduits, lighting fixtures, etc.) in cylinder storage rooms shall meet National Electrical Code (NFPA 70) requirements for hazardous areas.

# 3.0 Handling of Cylinders

- A cylinder shall never be lifted by its valve.

- A protective cap shall remain on the valve when the cylinder is not in use.

- A cylinder’s valve shall be fully closed before a cylinder is moved.

- Unless a trolley or special carrier is used, regulators and hoses shall be detached, and cylinder valve caps put back in place before moving.

- If cylinders are to be lifted by a crane, specially designed bottle carriers with lifting eyes shall be used, and shall not be lifted with electromagnetic devices, slings, chains, or ropes.

- Cylinders shall not be struck together, dropped, thrown, dragged, or used as rollers or as a support.

- Personnel handling toxic gas cylinders shall be trained in the hazards of the gas they are handling and how to use a self-contained breathing apparatus (SCBA).

- Empty cylinders shall be returned to the supplier with the valves closed and cylinder valve caps in place.

# 4.0 Transportation

- Cylinder trolleys, material baskets, cylinder racks, and other proper types of equipment shall be used to transport cylinders.

- All cylinders being transported by vehicle shall have cylinder valve caps in place, be positioned in an upright position, and be firmly secured to prevent movement.

- Vehicles transporting cylinders shall be equipped with the required firefighting and first aid equipment.

# Revision History

| Rev. | Date | Description of Change | Approved By |
| --- | --- | --- | --- |
| R01 | June 2026 | First issue — DAN HSE Minimum Requirement, adapted from the source OH&S minimum requirement, re-branded to DAN and coded to the DAN document-numbering convention (01-000001-000000-DAN-HSE-MNR-{seq}). | HSSE Manager |