HEALTH, SAFETY & ENVIRONMENT MANAGEMENT SYSTEM

DAN Construction Safety Manual (DCSM)

Fire Protection and Prevention

Document Control

| Document No. | 01-000001-000000-DAN-HSE-PRC-000020 | Revision | R01 |
| --- | --- | --- | --- |
| Issue Date | June 2026 | Classification | Controlled — Internal |
| Document Owner | HSE Department | Page Format | US Letter |

Table of Contents

1. Purpose

2. Scope

3. References

4. Deliverables

5. Fire Protection

5.1 Portable Fire Extinguishers

5.2 Standpipe and Hose Systems

5.3 Fixed Extinguishing Systems and Inspection

6. Fire Prevention

6.1 Site Layout

6.2 Storage

6.3 Control of Ignition Sources

6.4 Flammable and Combustible Liquids and Gases

6.5 Housekeeping

7. Training

8. Records

9. Related Documents

Figures and Illustrations

Revision History

# 1. Purpose

This document describes the requirements for fire protection and prevention on DAN projects and operating sites, including extinguishers, firefighting equipment and fire-warning systems. Fire-alarm, response, evacuation and exit-route requirements are integrated into the Emergency Planning and Response chapter.

# 2. Scope

This document applies to all DAN project and operating sites, covering both fire protection (equipment and systems) and fire prevention (layout, storage, ignition control and housekeeping).

# 3. References

- NFPA 10 (portable extinguishers); NFPA 14 (standpipe and hose); NFPA 30 (flammable liquids); NFPA 58 (LPG); NFPA 70 (NEC)

- 29 CFR 1910.155–.165; 29 CFR 1926.150–.159

- DCSM — Emergency Planning and Response

- DCSM — Materials Handling / Storage and COSHH

# 4. Deliverables

- Fire Protection Plan

- Fire Protection Equipment

# 5. Fire Protection

## 5.1 Portable Fire Extinguishers

Extinguishers are distributed per NFPA 10, available in convenient, accessible locations, and selected to match the class of fire hazard:

| Class | Hazard | Suitable Extinguishing Agents |
| --- | --- | --- |
| Class A | Ordinary combustibles (paper, wood, cloth, rubber, plastics) | Water, foam, loaded stream, or multipurpose dry chemical |
| Class B | Flammable/combustible liquids, gases and greases | CO₂, dry chemical, foam, loaded stream (or Halon 1301/1211) |
| Class C | Energised electrical equipment | CO₂ or dry chemical (electrically non-conductive media) |
| Class D | Combustible metals (magnesium, titanium, sodium, lithium) | Universal dry-powder agents (e.g. Lith-X, dry graphite, dry sand) |

Note:  Water, gas or certain dry chemicals cannot extinguish or control Class D fires.

## 5.2 Standpipe and Hose Systems

Acceptable standpipe systems may substitute for portable extinguishers where they provide the same coverage. Hoses are spaced to reach around obstructions and into enclosed areas; standpipes are protected from damage and stored in obstruction-free cabinets/covers, within reach without ladders, and designed and installed per NFPA 14. Unserviceable hose (dry-rotted, cross-threaded couplings, punctured) is removed from service.

## 5.3 Fixed Extinguishing Systems and Inspection

- Supervisors warn personnel of the hazards of fixed extinguishing systems (visual disorientation from dry-chemical clouds, hazardous combustion by-products from gaseous agents, hazardous post-discharge concentrations, liquid splatter).

- Carbon tetrachloride and chlorobromomethane are prohibited where personnel could be exposed (chlorobromomethane is acceptable only as an explosion-suppression agent in unoccupied spaces).

- A Competent Person inspects portable extinguishers (and respirators) at least monthly; when an extinguisher is removed from service, equivalent protection is provided (replacement units, a posted fire watch, restricted access or a ready hose system).

# 6. Fire Prevention

## 6.1 Site Layout

- Isolate or specially protect high-fire-risk operations (welding, open flame) from flammable/explosive materials.

- Provide fire-department/emergency access roads not less than 6 m (20 ft) wide with 5.5 m (18 ft) overhead clearance, kept unobstructed, with more than one access road where a single road could be impaired.

- Restrict flammable/combustible storage to the minimum necessary, meeting NFPA 30; provide NFPA 10 extinguishers of suitable type and number, clearly marked on the site layout.

## 6.2 Storage

- Outdoor storage: stack combustibles stably, no higher than 6 m (20 ft) and no stack larger than 141 m³; keep access roads at least 4.5 m (15 ft) wide; store flammables in a designated area away from ignition sources and separate from incompatible materials (e.g. oxidisers).

- Indoor storage: store per fire characteristics; segregate incompatible materials by a 1-hour-rated barrier; maintain ceiling clearance (0.6 m without sprinklers, 0.5 m below sprinkler heads) and clearance around lights, heating units and fire-rated doors; never obstruct exits or exit-sign visibility.

## 6.3 Control of Ignition Sources

- Install temporary wiring per NFPA 70 with GFCIs, and regularly check electrical equipment for defects; post and enforce “No Smoking” signs (smoking only in designated areas).

- Segregate welding equipment, asphalt kettles and other open flames from flammables; control indirect ignition (e.g. falling welding slag); open burning is prohibited without KSA Civil Defence authorisation.

- Use bonding and grounding where static could ignite; remove ignition sources immediately on a hydrocarbon leak; provide flameproof welding screens; all cutting/welding/burning requires a qualified fire watcher present during and for at least ½ hour after the work.

## 6.4 Flammable and Combustible Liquids and Gases

- Store flammable liquids in securely capped metal containers or steel drums, clearly marked; keep volatile liquids (flash point below 32 °C) in metal lockers in ventilated, non-combustible huts.

- Secure flammable storage areas at least 15 m (50 ft) from the nearest building, posting hazard signs and pictograms; observe outdoor stack limits (≤ 227 L/container, ≤ 4,160 L/area, 1.5 m separation, ≥ 6 m from structures) with a 3.6 m access way within 60 m.

- Transport flammable/combustible liquids only in closed, labelled, FM-approved or UL-listed metal containers (plastic prohibited); place portable gasoline containers on the ground during filling, never in passenger compartments, and never use gasoline as a cleaning agent.

- During transfer operations, separate from ignition sources by 25 ft or a 1-hour barrier, keep open flames 50 ft away, ground and bond containers, stop engines before refuelling, and prohibit mobile-phone use; store and use LPG per NFPA 58.

## 6.5 Housekeeping

- Remove waste from the worksite at regular intervals and at the end of each day; do not store combustibles under buildings or stairways.

- Provide metal bins with close-fitting lids for oily rags and combustible waste (oily rags kept separate); use non-combustible absorbents for oil spills and leaks.

# 7. Training

In-house authorised personnel are trained in fire awareness and response; the SH&E Representative arranges initial training, and supervisors communicate safe behaviour and controls at daily toolbox talks.

# 8. Records

The Fire Protection Plan, inspection records and training records are documented and maintained on-site for the duration of the project and archived at project close.

# 9. Related Documents

- DCSM — Emergency Planning and Response

- DCSM — Materials Handling / Storage and COSHH

- DCSM — Permit to Work (Hot Work)

- Fire Prevention Inspection Checklist

# Figures and Illustrations

Approved Flammable-Liquids Storage Cabinet

# Revision History

| Rev. | Date | Description of Change | Approved By |
| --- | --- | --- | --- |
| R00 | June 2026 | Initial issue. Restructured to the DAN integrated HSSE management-system template and re-branded in accordance with the DAN Brand Book. | Project Director |
| R01 | June 2026 | Re-coded to the updated DAN document-numbering convention (01-000001-000000-DAN-{discipline}-{type}-{seq}). | Project Director |