HEALTH, SAFETY & ENVIRONMENT MANAGEMENT SYSTEM

DAN Construction Safety Manual (DCSM)

Fire Protection and Prevention

Document Control

| Document No. | 01-DAN-PRC-HSE-000020-FIRPRT | Revision | R01 |
| --- | --- | --- | --- |
| Issue Date | June 2026 | Classification | Controlled — Internal |
| Document Owner | HSE Department | Page Format | US Letter |

Table of Contents

# 1. Purpose

This document describes the requirements for fire protection and prevention on DAN projects and operating sites, including extinguishers, firefighting equipment and fire-warning systems. Fire-alarm, response, evacuation and exit-route requirements are integrated into the Emergency Planning and Response chapter.

# 2. Scope

This document applies to all DAN project and operating sites, covering both fire protection (equipment and systems) and fire prevention (layout, storage, ignition control and housekeeping).

# 3. References

- NFPA 10 (portable extinguishers); NFPA 14 (standpipe and hose); NFPA 30 (flammable liquids); NFPA 58 (LPG); NFPA 70 (NEC)

- 29 CFR 1910.155–.165; 29 CFR 1926.150–.159

- DCSM — Emergency Planning and Response

- DCSM — Materials Handling / Storage and COSHH

# 4. Deliverables

- Fire Protection Plan

- Fire Protection Equipment

# 5. Fire Protection

## 5.1 Portable Fire Extinguishers

Extinguishers are distributed per NFPA 10, available in convenient, accessible locations, and selected to match the class of fire hazard:

| Class | Hazard | Suitable Extinguishing Agents |
| --- | --- | --- |
| Class A | Ordinary combustibles (paper, wood, cloth, rubber, plastics) | Water, foam, loaded stream, or multipurpose dry chemical |
| Class B | Flammable/combustible liquids, gases and greases | CO₂, dry chemical, foam, loaded stream (or Halon 1301/1211) |
| Class C | Energised electrical equipment | CO₂ or dry chemical (electrically non-conductive media) |
| Class D | Combustible metals (magnesium, titanium, sodium, lithium) | Universal dry-powder agents (e.g. Lith-X, dry graphite, dry sand) |

Note:  Water, gas or certain dry chemicals cannot extinguish or control Class D fires.

## 5.2 Standpipe and Hose Systems

Acceptable standpipe systems may substitute for portable extinguishers where they provide the same coverage. Hoses are spaced to reach around obstructions and into enclosed areas; standpipes are protected from damage and stored in obstruction-free cabinets/covers, within reach without ladders, and designed and installed per NFPA 14. Unserviceable hose (dry-rotted, cross-threaded couplings, punctured) is removed from service.

## 5.3 Fixed Extinguishing Systems and Inspection

- Supervisors warn personnel of the hazards of fixed extinguishing systems (visual disorientation from dry-chemical clouds, hazardous combustion by-products from gaseous agents, hazardous post-discharge concentrations, liquid splatter).

- Carbon tetrachloride and chlorobromomethane are prohibited where personnel could be exposed (chlorobromomethane is acceptable only as an explosion-suppression agent in unoccupied spaces).

- A Competent Person inspects portable extinguishers (and respirators) at least monthly; when an extinguisher is removed from service, equivalent protection is provided (replacement units, a posted fire watch, restricted access or a ready hose system).

# 6. Fire Prevention

## 6.1 Site Layout

- Isolate or specially protect high-fire-risk operations (welding, open flame) from flammable/explosive materials.

- Provide fire-department/emergency access roads not less than 6 m (20 ft) wide with 5.5 m (18 ft) overhead clearance, kept unobstructed, with more than one access road where a single road could be impaired.

- Restrict flammable/combustible storage to the minimum necessary, meeting NFPA 30; provide NFPA 10 extinguishers of suitable type and number, clearly marked on the site layout.

## 6.2 Storage

- Outdoor storage: stack combustibles stably, no higher than 6 m (20 ft) and no stack larger than 141 m³; keep access roads at least 4.5 m (15 ft) wide; store flammables in a designated area away from ignition sources and separate from incompatible materials (e.g. oxidisers).

- Indoor storage: store per fire characteristics; segregate incompatible materials by a 1-hour-rated barrier; maintain ceiling clearance (0.6 m without sprinklers, 0.5 m below sprinkler heads) and clearance around lights, heating units and fire-rated doors; never obstruct exits or exit-sign visibility.

## 6.3 Control of Ignition Sources

- Install temporary wiring per NFPA 70 with GFCIs, and regularly check electrical equipment for defects; post and enforce “No Smoking” signs (smoking only in designated areas).

- Segregate welding equipment, asphalt kettles and other open flames from flammables; control indirect ignition (e.g. falling welding slag); open burning is prohibited without KSA Civil Defence authorisation.

- Use bonding and grounding where static could ignite; remove ignition sources immediately on a hydrocarbon leak; provide flameproof welding screens; all cutting/welding/burning requires a qualified fire watcher present during and for at least ½ hour after the work.

## 6.4 Flammable and Combustible Liquids and Gases

- Store flammable liquids in securely capped metal containers or steel drums, clearly marked; keep volatile liquids (flash point below 32 °C) in metal lockers in ventilated, non-combustible huts.

- Secure flammable storage areas at least 15 m (50 ft) from the nearest building, posting hazard signs and pictograms; observe outdoor stack limits (≤ 227 L/container, ≤ 4,160 L/area, 1.5 m separation, ≥ 6 m from structures) with a 3.6 m access way within 60 m.

- Transport flammable/combustible liquids only in closed, labelled, FM-approved or UL-listed metal containers (plastic prohibited); place portable gasoline containers on the ground during filling, never in passenger compartments, and never use gasoline as a cleaning agent.

- During transfer operations, separate from ignition sources by 25 ft or a 1-hour barrier, keep open flames 50 ft away, ground and bond containers, stop engines before refuelling, and prohibit mobile-phone use; store and use LPG per NFPA 58.

## 6.5 Housekeeping

- Remove waste from the worksite at regular intervals and at the end of each day; do not store combustibles under buildings or stairways.

- Provide metal bins with close-fitting lids for oily rags and combustible waste (oily rags kept separate); use non-combustible absorbents for oil spills and leaks.

# 7. Training

In-house authorised personnel are trained in fire awareness and response; the SH&E Representative arranges initial training, and supervisors communicate safe behaviour and controls at daily toolbox talks.

# 8. Records

The Fire Protection Plan, inspection records and training records are documented and maintained on-site for the duration of the project and archived at project close.

# 9. Related Documents

- DCSM — Emergency Planning and Response

- DCSM — Materials Handling / Storage and COSHH

- DCSM — Permit to Work (Hot Work)

- Fire Prevention Inspection Checklist

# Figures and Illustrations

Approved Flammable-Liquids Storage Cabinet

# Revision History

| Rev. | Date | Description of Change | Approved By |
| --- | --- | --- | --- |
| R00 | June 2026 | Initial issue. Restructured to the DAN integrated HSSE management-system template and re-branded in accordance with the DAN Brand Book. | Project Director |
| R01 | June 2026 | Re-coded to the updated DAN document-numbering convention (01-DAN-PRC-HSE-{seq}{code}). | Project Director |